Tender text GEZE MCRdrive
                        Version V01
Status: 22.10.24
	Project:
	

	Support:
	

	Spec. No.
	
	Site:
	


	Pos-Nr.
	Quantity
	Unit
	Unit Price
	
	Total amount
	



	1.0 
	.........................  pcs.                  ..............................  €             ..............................  €

GEZE MCRdrive hermetic sliding door system
GEZE MCRdrive automatic hermetically sealing linear sliding door system for indoor areas with air permeability requirements in accordance with EN 1026 / EN 12207, class D at 150 Pa. Sound insulation in accordance with DIN EN ISO 4109, up to 37 dB. TÜV type-tested in accordance with DIN 18650 / EN 16005, for leaf weights up to 200 kg.
The system consists of the main components:

- Drive unit with special software, with optimised opening widths for hospital operation (nurse,
  cleaning and bed opening), Push & Go function 

- Universal, fine-framed profile system for different door leaf fillings, for the realisation of slim
  contours and large glass surfaces

- Circumferential gasket system with vulcanised gasket corners reduces the air permeability
  of the closed sliding door system

- Hermetic sealing by lowering and pressing the door leaf against the frame construction
  Door leaf versions in glass, stainless steel or HPL

Construction dimensions (unfinished state):
Passage width DB:............. mm (800 - 2500 mm)
Passage height DH:..............     mm (2000 – 2400 mm standard)

Further dimensions on request.

Door system version:
(  ) single leaf left closing
(  ) single leaf right closing
Surface of the system:
(  ) RAL
(  ) EV1



	1.1 
	.........................  pcs.                  ..............................  €             ..............................  €

GEZE MCRdrive drive unit and GEZE control unit
Dimensions of drive unit H x D: 200 x 200 mm
Automatic door drive consisting of:
· Extremely smooth-running DC drive with integrated rechargeable battery with automatic charging and monitoring system

· Robust power supply with integrated all-pole main switch and fuse protection. Static and dynamic force limitation in accordance with DIN 18650 / EN 16005 and static under 150 N in accordance with ASR A1.7 (formerly BGR 232)

· Intelligent control (category 2 in accordance with DIN EN 954-1 and Performance Level “D” in accordance with DIN EN ISO 13849-1)

· Convenient setting of freely selectable parameters, commissioning and maintenance via optional Bluetooth connection to a PC

· Self-learning with dynamic adaptation of the passage hold-open time for optimum convenience

· Can be networked and integrated into building management systems

· Autonomous fault detection and logging

· Setting options for all door movement parameters

· All functions integrated in one unit, no additional modules required

· Automatic reversing on obstacle detection

· Aluminium track and roller carriage with plastic rollers, including articulated joint for lowering and pressing the door leaf against the wall connection profile for hermetic sealing

Drive functions:
· Various Push & Go functions available
· Parameters for inputs and outputs for different functions can be freely set
· Integrated rechargeable battery for emergency opening and closing in the event of a power failure

· Various opening types and widths optimised for use in medical areas:

- Bed opening for full opening width

- Full opening for permanent opening

- Personnel opening for reduced opening width

The standard cover design is provided in aluminium. 
The following cover designs are available on customer request: 

( ) Standard made of aluminium 

( ) Stainless steel cover
Wiring to be carried out on site according to the GEZE cable plan by an electrical contractor.
Installation, commissioning and instruction of the operator as well as documentation handover in compliance with DIN 18650 / EN 16005 through GEZE personnel or service partner.
In accordance with DIN 18650 / EN 16005:
· Safety analysis must be carried out as a basis for planning and execution
· An inspection and maintenance must be carried out at least once a year



	1.2 
	.........................  pcs.                  ..............................  €             ..............................  €

GEZE MCRdrive door leaf designs, profile and gasket system
The air tightness and sealing, in accordance with air permeability requirements according to EN 1026 / EN 12207 Class D at 150 Pa, is realised on all four leaf sides by a lowering and simultaneous pressure movement of the leaf against the on-site frame. The circumferential gasket system consists of a special balloon gasket and a concealed 2-chamber gasket in the base area. The circumferential gasket guide is implemented using vulcanised gasket corners. The gaskets are installed in profile-integrated gasket grooves.
( ) Glass door leaf with the following design

( ) LSG 10 mm consisting of 2 x 5 mm toughened safety glass, clear 

( ) LSG 10 mm consisting of 2 x 5 mm toughened safety glass, satin finish
( ) LSG 10 mm consisting of 2 x 5 mm toughened safety glass, clear incl. sound insulation 
    film 37 dB 

( ) LSG 10 mm consisting of 2 x 5 mm toughened safety glass, satin finish incl. sound
    insulation film 37 dB 

( ) ISO 22 mm consisting of 2 x 5 mm toughened safety glass, clear, Ug value 3.0 W/(m²K)

( ) HPL door leaf 

( ) 22 mm HPL panel framed in GEZE MCRdrive profile system

( ) HPL panel flush-mounted

( ) Stainless steel leaf

Special options for door leaf designs

X-ray protection

( ) 1 mm Pb 

( ) 2 mm Pb 

View window

( ) 400 x 400 mm

( ) 400 x 600 mm

( ) individual dimension

Additional manual operation

( ) knob

( ) bar handle

The glazing can be designed both as dry glazing with system-side gaskets for different panel thicknesses, or as wet glazing.



	1.3 
	.........................  pcs.                  ..............................  €             ..............................  € 

GEZE MCRdrive frame options

( ) Frame provided by customer

( ) Stainless steel surrounding frame

Other frame designs available on request.


	1.4 
	.........................  pcs.                  ..............................  €             ..............................  €

Control and protection

GEZE GC 339+ light curtain for controlling and protecting automatic sliding doors with ten adjustable light curtain configurations. Reliable detection up to an installation height of 3500 mm. All settings can be made by remote control.

( ) Interior light curtain ( ) Exterior light curtain

or

GEZE GC 363+ combined detector for controlling and protecting automatic sliding doors with ten adjustable light curtain configurations, with infrared light curtain, direction of movement detection and cross-traffic fade-out reduces energy consumption in the building. All settings can be made by remote control. Reliable detection up to a mounting height of 3500 mm.
( ) Combined detector inside ( ) Combined detector outside

or

GEZE GC 365 combined detector for controlling and protecting automatic sliding doors with four adjustable light curtain configurations, lookback function secures the area between the door leaves during the hold-open time, instructions for installation and parameterisation are located directly in the sensor housing. Reliable detection up to an installation height of 3500 mm.
( ) Combined detector inside ( ) Combined detector outside

Activation button

( ) GC 307+ non-contact proximity switch for activating automatic doors. Doors can be opened without the need for haptic perception, can also be installed behind tiles or glass.
or

( ) Hygienic Package LED sensor switch
One switch each for controlling the programmable door leaf opening width in person opening = full opening width, cleaning opening = permanently open, bed opening = reduced opening width.

All GEZE standard control units and sensors for automatic sliding doors are compatible. Other activation buttons available on request.



	1.5 
	.........................  pcs.                  ..............................  €             ..............................  €

Operation
GEZE DPS display programme switch for setting the mode of operation for automatic doors and for commissioning and for setting the parameters of the drive, with control keys, 2 x 7-segment display, alphanumeric error display, protection class IP40

Modes of operation: permanently open, automatic, exit only, night locking, off

( ) AP ( ) UP

or 

GEZEconnects Bluetooth RS485 interface for the wireless connection between computer and automatic GEZE door drives.


Source: GEZE GmbH, Reinhold-Vöster-Str. 21-29, D-71229 Leonberg, Web: www.geze.com

Tel.: 07152-203-0, Fax: 07152-203-310, E-Mail: info.de@geze.com

